## Info
© 2018 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
31-08-18
OJ-AHC-3000
Modbus protocol
Software version 1.00
Quick overview
The most common used parameters.
Modbus Info
General information about modbus RTU/TCP-IP
Modbus RTU Connection
How to connect Modbus RTU (RS-485)
Parameters
Complete list of all Modbus parameters.

## Quick overview
Modbus overview
Quick overview over the most used parameters |  |  |  |  | Exhaust | Modbus
[5 empty] | Current exhaust air temp. [1/100°C] | 3x0031 | R
[5 empty] | Current extract flow [l/s] | 3x0009 | R
[5 empty] | Extract air motor output percentage (OJ-DV) [1/100%] | 3x0014 | R
[5 empty] | Setpoint for extract flow, low speed [l/s] | 4x0019 | RW
[5 empty] | Setpoint for extract flow, medium speed [l/s] | 4x0020 | RW
[5 empty] | Setpoint for extract flow, high speed [l/s] | 4x0021 | RW
[5 empty] | Heat Exchanger | Modbus
[5 empty] | Heat exchanger (Cross & Counter flow/3. part) (0-10V) – output percent. [%] | 3x0046 | R
[5 empty] | Outdoor air | Modbus
[5 empty] | Current outdoor temp. (AHU internal sensor) [1/100°C] | 3x0029 | R
[5 empty] | Outdoor air filter; current pressure drop [Pa] | 3x0038 | R
[5 empty] | Extract | Modbus
[5 empty] | Current extract air temperature [1/100°C] | 3x0027 | R
[5 empty] | Extract air filter; current pressure drop [Pa] | 3x0037 | R
[5 empty] | Current CO2 value [ppm] (0-10V=0-2000ppm) | 3x0011 | R
[5 empty] | Current VOC value from the VOC sensor (VTH-6202) | 3x0012 | R
[5 empty] | Current humidity value from the humidity sensor (HTH-6202) [1/100°C | 3x0171 | R
[5 empty] | Current room temperature [1/100 °C] | 3x0030 | R
[5 empty] | Current extract duct pressure [Pa] | 3x0005 | R
[5 empty] | Setpoint for duct pressure, extract, low speed [Pa] | 4x0010 | RW
[5 empty] | Setpoint for duct pressure, extract, medium speed [Pa] | 4x0011 | RW
[5 empty] | Setpoint for duct pressure, extract, high speed [Pa] | 4x0012 | RW
[5 empty] | Supply | Modbus
[5 empty] | Current supply air temperature [1/100°C] | 3x0025 | R
[5 empty] | Select temperature control mode; 1=Supply, 2=Extract, 3=Room | 4x0090 | RW
[5 empty] | Temperature setpoint for control mode: Supply air temperature [1/100°C] | 4x0091 | RW
[5 empty] | Temperature setpoint for control mode: Extract temperature [1/100°C] | 4x0092 | RW
[5 empty] | Temperature setpoint for control mode: Room temperature [1/100°C] | 4x0093 | RW
[5 empty] | Min. limit, supply air temp. [1/100°C] | 4x0094 | RW
[5 empty] | Max. limit, supply air temp. [1/100°C] | 4x0095 | RW
|  | Controls | Modbus |  | Current heating power [1/100%] | 3x0047 | R
|  | Current operating mode | 3x0001 | R | Heating relay 1 | 1x0031 | R
|  | Operation ON/OFF | 1x0001 | R | Current heating coil temp. (Return pipe sensor) [1/100°C] | 3x0034 | R
|  | Extended high speed (Boost) –> Active | 1x0005 | R | Current cooling power [1/100%] | 3x0048 | R
|  | Minimum one A-alarm triggered | 1x0033 | R | Supply air motor output percentage (OJ-DV) [1/100%] | 3x0013 | R
|  | Minimum one B-alarm triggered | 1x0034 | R | Current supply flow [l/s] | 3x0007 | R
|  | Alarm reset signal (AutoReturn to zero) | 0x0001 | RW | Setpoint for supply flow, low speed [l/s] | 4x0015 | RW
[5 empty] | Setpoint for supply flow, medium speed [l/s] | 4x0016 | RW
[5 empty] | Setpoint for supply flow, high speed [l/s] | 4x0017 | RW
[5 empty] | Current supply duct pressure [Pa] | 3x0003 | R
[5 empty] | Setpoint for supply duct pressure, low speed [Pa] | 4x0004 | RW
[5 empty] | Setpoint for supply duct pressure, medium speed [Pa] | 4x0005 | RW
[5 empty] | Setpoint for supply duct pressure, high speed [Pa] | 4x0006 | RW
R=Read only
RW=Read & Write
© 2018 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
31-08-18

## Modbus info
Modbus RTU/TCP-IP
OJ-AHC-3000, Program version 1.00 and later versions
Overview
This Protocol contains all Modbus addresses and registers in the OJ-AHC-3000 controller.
Updating of values in the individual registers is dependent on the actual configuration of the air handling unit.
It will, for example, be possible to read out water heating coil temperature (Register 3x0034) irrespective of
whether or not an water heating coil is installed in the system concerned.
In the SW the value will, however, only be used if the water heating coil and the temperature sensor is installed.
Modbus can access single addresses or several addresses simultaneously,
either reading or writing 1-bit or 16-bit values.
A Modbus address contains either a 1-bit value or a 16-bit integer.
Communication ports
TCP/IP: 1 x 10/100 Mbit Ethernet, RJ45 connector.
BMS (RS485): 1 x external Modbus, RS485, RJ12 connector, which can be set for 9.6 kBaud, 19.2 kBaud or 38.4 kBaud.
RJ12Connections: Pin1: NC, Pin2: GND, Pin3: RS485 B, Pin4: RS485 A, Pin5: NC, Pin6: GND (NC=Not connected)
Standard Modbus TCP/IP Communikation port: 502
IP-address: 192.168.1.100 (Static)*
Netmask: 255.255.255.0*
*=Factory settings
Modbus data format
Modbus data types are 1-bit values and 16-bit values.
Modbus Type |  | Description | Reference
Coil Status (R/W) |  | Discrete Output | 0x
Input Status (R) |  | Discrete Input | 1x
Holding Register (R/W) |  | 16-bit Output Register | 4x
Input register (R) |  | 16-bit Input Register | 3x
R = Read Only
R/W = Read / Write
Supported Modbus commands
OJ Air2 supports the following Modbus commands:
Function code | Description
1 | Read Coil Status
2 | Read Input Status
3 | Read Holding Registers
4 | Read Input Registers
5 | Force Single Coil
6 | Preset Single Registers
8 | Diagnostics. Sub-function 00 Only - Return Query Data (loop back)
15 | Force Multiple Coils
16 | Preset Multiple Registers
© 2018 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
31-08-18

## Modbus Overview parameters (hidden)
Actual extract flow [l/s] |  |  | 3x0009
Extract motor output percentage [1/100%] |  |  | 3x0083 |  |  |  | Actual operating mode | 3x0001
Setpoint for extract flow, low speed [l/s] |  |  | 4x0014 |  |  |  | Operation ON/OFF | 1x0001
Setpoint for extract flow, high speed [l/s] |  |  | 4x0015 |  |  |  | Extended low speed –> Active | 1x0004
[7 empty] | Extended high speed –> Active | 1x0005
|  | Actual extract duct pressure [Pa] |  | 3x0005 |  |  | Alarm relay 1 (A-alarm) | 1x0035
|  | Setpoint for duct pressure, extract, low speed [Pa] |  | 4x0007 |  |  | Alarm relay 2 (B-alarm) | 1x0036
|  | Setpoint for duct pressure, extract, high speed [Pa] |  | 4x0008 |  |  | Alarm reset signal (AutoReturn to zero) | 0x0001
|  | Inlet filter pressure [Pa] |  | 3x0031
|  | Inlet filter monitor max. alarm limit [Pa] |  | 3x0039
[7 empty] | Actual inlet temperature [1/100°C] | 3x0020
[7 empty] | Control type setting | 4x0148
[7 empty] | Temperature setpoint for actual control type | 4x0149
[7 empty] | Extract filter pressure [Pa] | 3x0032
[7 empty] | Max. alarm limit, extract filter pressure drop [Pa] | 3x0040
[7 empty] | Actual room temperature [1/100 °C] | 3x0025
[7 empty] | Actual exhaust temp. [1/100°C] | 3x0026
[7 empty] | Min. limit, inlet temp. [1/100°C] | 4x0150
[7 empty] | Max. limit, inlet temp. [1/100°C] | 4x0151
[7 empty] | Actual inlet duct pressure [Pa] | 3x0003
[7 empty] | Setpoint for duct pressure, inlet, low speed [Pa] | 4x0003
[7 empty] | Setpoint for duct pressure, inlet, high speed [Pa] | 4x0004
[7 empty] | Actual inlet flow [l/s] | 3x0007
[7 empty] | Inlet motor output percentage [1/100%] | 3x0073
[7 empty] | Setpoint for inlet flow, low speed [l/s] | 4x0011
[7 empty] | Setpoint for inlet flow, high speed [l/s] | 4x0012
Actual outdoor temp. [1/100°C] 3x0024 |  |  |  |  | Actual heating power [1/100%] | 3x0054
[5 empty] | Heating relay 1 | 1x0031
| Rot. heat exchanger – output percent. [%] |  | 3x0092 |  | Act. heating bat. temp.[1/100°C] | 3x0030
|  |  | Actual cooling power [1/100%] |  | 3x0056
© 2016 OJ Electronics A/S · ® The Trade Mark OJ is an registered Trade Mark belonging to OJ Electronics A/S
06-07-16

## Modbus RTU Connection
© 2018 OJ Electronics A/S · ® The OJ trademark is a registered trademark belonging to OJ Electronics A/S
OJ AHC-3000 Controller
RJ12 Modbus/RTU connection
Fig. 1 OJ-AHC-3000, Connector diagram, visualized from the frontside
Fig. 3 Modbus RTU RJ12 socket
Fig. 2 Configuration for communication via external Modbus
31-08-18
Communication over external Modbus RTU / RS485
- NC
- NC
*- NC = Not Connected

## Parameters
Intern ID | Component | Function | Standard/ Special | Name | SI Unit | Modbus register | SW vers. | Min | Max | Factory settings | Description | Dansk | English
| 1. Info | 1. Info | 1. Info | 1. Info |  | Coil status (R/W)
| AHU controller | Alarm | Standard | AL_ManResetAll |  | 0x0001 | 1.00 | 0 | 1 | 0 |  |  | Alarm reset signal (AutoReturn to zero)
| AHU controller | Summer Night Cooling | Standard | SN_Func_UserSet |  | 0x0003 | 1.00 | 0 | 1 | 0 |  |  | Summer night cooling: ON/OFF
| 1. Info | 1. Info | 1. Info | 1. Info |  | Input status (R) |  | 1. Info | 1. Info | 1. Info
| AHU controller | Speed | Standard | IOC_DO_Operation_Set |  | 1x0001 | 1.00 | 0 | 1 |  |  |  | Operation ON/OFF
| AHU controller | Speed | Standard | IOC_DI_Ext_Stop_Read |  | 1x0002 | 1.00 | 0 | 1 |  |  |  | External stop
| AHU controller | Speed | Standard | IOC_DI_ExtHigh_Read |  | 1x0003 | 1.00 | 0 | 1 |  |  |  | Externalhigh speed
| AHU controller | Speed | Standard | AB_Active |  | 1x0005 | 1.00 | 0 | 1 |  |  |  | Extended high speed –> Active (AHC-3000 : Boost)
| Electric heating coil | Status | Standard | HT_RH_ReductionActive |  | 1x0010 | 1.00 | 0 | 1 |  |  |  | Power to electric heating coil reduced due to low flow
| AHU controller | Summer Night Cooling | Standard | SN_Active |  | 1x0011 | 1.00 | 0 | 1 |  |  |  | Summer night cooling is active
| Rotary Heat Exchanger | Speed | Standard | RX_PO_Active |  | 1x0017 | 1.00 | 0 | 1 |  |  |  | Exercising heat exchanger –> Active, (AHC-3000 : periodical operation, PO, DRHX)
| Heat Exchanger | Status | Standard | PX_DF_State |  | 1x0018 | 1.00 | 0 | 1 |  |  |  | Signal to cross-flow exchanger reduced (frost protection)
| AHU controller | Status | Standard | PR_SA_MaxSpeedActive |  | 1x0020 | 1.00 | 0 | 1 |  |  |  | Supply duct pressure controller increased to max. flow
| AHU controller | Status | Standard | PR_EA_MaxSpeedActive |  | 1x0022 | 1.00 | 0 | 1 |  |  |  | Extract duct pressure controller increased to max. flow
| AHU controller | Status | Standard | CL_CR_Active |  | 1x0023 | 1.00 | 0 | 1 |  |  |  | Cooling recovery –> status
| Water Heating Coil | Status | Standard | HT_RH_FP_RegActive |  | 1x0024 | 1.00 | 0 | 1 |  |  |  | Circulation pump on heating coil: Frost protection –> Active
| Water Heating Coil | Status | Standard | HT_RH_PO_Pump_Active |  | 1x0025 | 1.00 | 0 | 1 |  |  |  | Circulation pump on heating coil: Pump exercising –> Active
| Water Cooling Coil | Status | Standard | CL_RC_PO_Pump_Active |  | 1x0026 | 1.00 | 0 | 1 |  |  |  | CoolWaterCoil PumpExercise active
| AHU controller | Status | Standard | AR_FlowDownActive |  | 1x0027 | 1.00 | 0 | 1 |  |  |  | Signal to heating coil reduced (insufficient flow) –> Active
| AHU controller | Status | Standard | TR_SA_MinSupTempAct |  | 1x0028 | 1.00 | 0 | 1 |  |  |  | "1" when min. supply temperature control is active. Only active when TempRegMode is 1 or 2 (room temp. control)
| AHU controller | Status | Standard | TR_SA_MaxSupTempAct |  | 1x0029 | 1.00 | 0 | 1 |  |  |  | "1" when max. supply temperature control is active. Only active when TempRegMode is 1 or 2 (room temp. control)
| AHU controller | Status | Standard | IOC_DO_HT1_RE1_Set |  | 1x0031 | 1.00 | 0 | 1 |  |  |  | Heating relay 1
| AHU controller | Status | Standard | IOC_DO_CL1_RE1_Set |  | 1x0032 | 1.00 | 0 | 1 |  |  |  | Cooling relay 1
| AHU controller | Alarm | Standard | AL_Priority_A_Triggered |  | 1x0033 | 1.00 | 0 | 1 |  |  |  | At least one active alarm, A-Alarm >> New in AHC-3000
| AHU controller | Alarm | Standard | AL_Priority_B_Triggered |  | 1x0034 | 1.00 | 0 | 1 |  |  |  | At least one active alarm, B-Alarm
| AHU controller | Fire | Standard | IOC_DI_Ext_Fire_Read |  | 1x0037 | 1.00 | 0 | 1 |  |  |  | Fire alarm signal (room sensor)
| AHU controller | Smoke | Standard | IOC_DI_Ext_Smoke_Read |  | 1x0038 | 1.00 | 0 | 1 |  |  |  | Smoke/fire alarm signal (duct sensor)
| AHU controller | Status | Standard | TR_CL_RC_Available |  | 1x0040 | 1.00 | 0 | 1 |  |  |  | Coolsource available
| AHU controller | Status | Standard | TR_CL_HX_Available |  | 1x0041 | 1.00 | 0 | 1 |  |  |  | EXC as Coolsource available
| AHU controller | Status | Standard | TR_HT_HX_Available |  | 1x0042 | 1.00 | 0 | 1 |  |  |  | EXC as Heatsource available
| AHU controller | Status | Standard | TR_HT_RH_Available |  | 1x0043 | 1.00 | 0 | 1 |  |  |  | Heatsource available
| AHU controller | Status | Standard | TR_HT_FlowDnRegAvailable |  | 1x0044 | 1.00 | 0 | 1 |  |  |  | Flowdown available
| Rotary Heat Exchanger | Status | Standard | DRHX_DriftON |  | 1x0050 | 1.00 | 0 | 1 |  |  |  | Rotary heat exchanger – motor control ON/OFF (only with OJ-RHX2M)
| Rotary Heat Exchanger | Alarm | Standard | DRHX_RotorAlr |  | 1x0053 | 1.00 | 0 | 1 |  |  |  | Rotary heat exchanger – rotation alarm (only with OJ-DRHX)
| Common Fan, Supply | Alarm | Standard | AH_Common_SA_Fan |  | 1x0055 | 1.00 | 0 | 1 |  |  |  | Common Alarm SA Fan
| Common Fan, Supply | Alarm | Standard | AH_Common_SA_FwDu |  | 1x0056 | 1.00 | 0 | 1 |  |  |  | Common Alarm SA Pressure / Flow
| Common Fan, Exhaust | Alarm | Standard | AH_Common_EA_Fan |  | 1x0057 | 1.00 | 0 | 1 |  |  |  | Common Alarm EA/EXH Fan
| Common Fan, Exhaust | Alarm | Standard | AH_Common_EA_FwDu |  | 1x0058 | 1.00 | 0 | 1 |  |  |  | Common Alarm EA/EXH Pressure / Flow
| Common Circulation Pumps | Alarm | Standard | AH_Common_Pumps |  | 1x0059 | 1.00 | 0 | 1 |  |  |  | Common Alarm Circulation Pump
| Common Heat Exchanger | Alarm | Standard | AH_Common_RXCX |  | 1x0060 | 1.00 | 0 | 1 |  |  |  | Common Alarm Exchanger
| Common Frost | Alarm | Standard | AH_Common_Frost |  | 1x0061 | 1.00 | 0 | 1 |  |  |  | Common Alarm Frost HW/CMB Coil
| Common El-Heating-Coil | Alarm | Standard | AH_Common_ElCoil |  | 1x0062 | 1.00 | 0 | 1 |  |  |  | Common Alarm Electric heating coil
| Common Temperature | Alarm | Standard | AH_Common_Tmp_H_L |  | 1x0063 | 1.00 | 0 | 1 |  |  |  | Common Alarm temperature high/low
| Common Filter, Outdoor | Alarm | Standard | AH_Common_FM_OA |  | 1x0064 | 1.00 | 0 | 1 |  |  |  | Common Alarm OA Filter
| Common Filter, Extract | Alarm | Standard | AH_Common_FM_EA |  | 1x0065 | 1.00 | 0 | 1 |  |  |  | Common Alarm EA Filter
| Common Temp. Sensors | Alarm | Standard | AH_Common_T_Sensor |  | 1x0066 | 1.00 | 0 | 1 |  |  |  | Common Alarm Temperature Sensors
| Common Intern MB | Alarm | Standard | AH_Common_Intern_MB |  | 1x0068 | 1.00 | 0 | 1 |  |  |  | Common Alarm Com. Intern Modbus
| Fan, Supply | Status | Standard | BMS_SA_Fan_On |  | 1x0075 | 1.00 | 0 | 1 |  |  |  | Supply motor ON/OFF (0-10V Type)
| Fan, Supply | Alarm | Standard | BMS_SA_Fan_Alr_Inp |  | 1x0076 | 1.00 | 0 | 1 |  |  |  | Supply Motor Alarm, Dig. Input (0-10V Type)
| Fan, Exhaust | Status | Standard | BMS_EA_Fan_On |  | 1x0080 | 1.00 | 0 | 1 |  |  |  | Extract motor ON/OFF (0-10V Type)
| Fan, Exhaust | Alarm | Standard | BMS_EA_Fan_Alr_Inp |  | 1x0081 | 1.00 | 0 | 1 |  |  |  | Extract Motor Alarm, Dig. Input (0-10V Type)
| Damper, Outdoor & Exhaust | Status | Standard | IOC_DO_Damper_Set |  | 1x0085 | 1.00 | 0 | 1 |  |  |  | Output for outdoor air/exhaust air active, dig.Out Damper
| AHU controller | Status | Standard | IOC_DI_Ext_Start_Read |  | 1x0090 | 1.00 | 0 | 1 |  |  |  | Status external start input
| 1. Info | 1. Info | 1. Info | 1. Info |  | Input register (R) |  | 1. Info | 1. Info | 1. Info |  |  | 1. Info
| AHU controller | Control | Standard | OL_AHU_State |  | 3x0001 | 1.00 | 0 | 499 |  |  |  | Actual operating mode 000-099: Unit stopped 100-199: Unit in low speed mode 200-299: Unit in medium speed mode 300-399: Unit in high speed mode 400-499: Unit in spec. control mode
| Pressure | Current value | Standard | IOC_PS_SA_DU_Read |  | 3x0003 | 1.00 | 0 | 25000 |  |  |  | Actual supply duct pressure [1/10 Pa]
| Pressure | Set point | Standard | PR_SA_Reg_Set |  | 3x0004 | 1.00 | 0 | 7500 |  |  |  | Setpoint for supply duct pressure controller [1/10 Pa]
| Pressure | Current value | Standard | IOC_PS_EA_DU_Read |  | 3x0005 | 1.00 | 0 | 25000 |  |  |  | Actual extract duct pressure [1/10 Pa]
| Pressure | Set point | Standard | PR_EA_Reg_Set |  | 3x0006 | 1.00 | 0 | 7500 |  |  |  | Setpoint for extract duct pressure controller [1/10 Pa]
| Flow | Current value | Standard | SA_Flow |  | 3x0007 | 1.00 | 100 | 30000 |  |  |  | Actual supply flow [l/s]
| Flow | Set point | Standard | AR_SA_Reg_Set |  | 3x0008 | 1.00 |  | AR_SA_MS_UserSet |  |  |  | Setpoint for supply flow controller [l/s]
| Flow | Current value | Standard | EA_Flow |  | 3x0009 | 1.00 | 100 | 30000 |  |  |  | Actual extract flow [l/s]
| Flow | Set point | Standard | AR_EA_Reg_Set |  | 3x0010 | 1.00 | 0 | AR_EA_MS_UserSet |  |  |  | Setpoint for extract flow controller [l/s]
| CO2 sensor | Current value | Standard | CO2_SensorSignal |  | 3x0011 | 1.00 | 0 | 2000 |  |  |  | CO2 concentration recorded by CO2 sensor [ppm]
| VOC | Current value | Standard | VOC_Level |  | 3x0012 | 1.00 | 0 | 8000 |  |  |  | VOC concentration recorded by VOC sensor [ppm]
| Fan, Supply | Current value | Standard | HMI35_SA_Procent |  | 3x0013 | 1.00 | 0 | 10000 |  |  |  | Percent-Output to SA [1/100%], DV / 0-10V
| Fan, Exhaust | Current value | Standard | HMI35_EA_Procent |  | 3x0014 | 1.00 | 0 | 10000 |  |  |  | Percent-Output to EA [1/100%], DV / 0-10V
| Flow | Set point | Standard | AHU_SA_MaxFlow |  | 3x0017 | 1.00 | 0 | 30000 |  |  |  | Supply FC max. flow [l/s]
| Flow | Set point | Standard | AHU_EA_MaxFlow |  | 3x0018 | 1.00 | 0 | 30000 |  |  |  | Extract FC max. flow [l/s]
| Temp. Supply | Current value | Standard | AHU_SA_Temp |  | 3x0025 | 1.00 | -5500 | 12500 |  |  |  | Actual supply temperature [1/100°C]
| Temp. Supply | Set point | Standard | TR_SA_TempRegSet |  | 3x0026 | 1.00 | 0 | 4000 |  |  |  | Setpoint for supply temperature controller [1/100°C]
| Temp. Extract | Current value | Standard | AHU_EA_Temp |  | 3x0027 | 1.00 | -5500 | 12500 |  |  |  | Actual extract temperature [1/100°C]
| Temp. Extract | Set point | Standard | TR_EA_TempRegSet |  | 3x0028 | 1.00 | 500 | 4000 |  |  |  | Setpoint for extract temperature controller [1/100°C]
| Temp. Outdoor | Current value | Standard | AHU_OA_Temp |  | 3x0029 | 1.00 | -5500 | 12500 |  |  |  | Actual outdoor temperature [1/100°C]
| Temp. Room | Current value | Standard | AHU_RM_Temp |  | 3x0030 | 1.00 | 0 | 4000 |  |  |  | Actual room temperature [1/100°C]
| Temp. Exhaust | Current value | Standard | AHU_EXH_Temp |  | 3x0031 | 1.00 | -5500 | 12500 |  |  |  | Actual exhaust temperature [1/100°C]
| Temp. Heating Coil | Current value | Standard | AHU_HWR_Temp |  | 3x0034 | 1.00 | -5500 | 12500 |  |  |  | Actual heating coil temperature [1/100°C]
| Fan, Supply Pressure | Current value | Standard | IOC_PS_SA_FW_Read |  | 3x0035 | 1.00 | 0 | 25000 |  |  |  | Supply Fan pressure [1/10 Pa]
| Fan, Extract Pressure | Current value | Standard | IOC_PS_EA_FW_Read |  | 3x0036 | 1.00 | 0 | 25000 |  |  |  | Exhaust Fan pressure [1/10 Pa]
| Filter, Extract pressure | Current value | Standard | IOC_PS_SF_EA_FM_Read |  | 3x0037 | 1.00 | 0 | 25000 |  |  |  | Extract filter pressure [1/10 Pa]
| Filter, Outdoor pressure | Average value | Standard | IOC_PS_SF_OA_FM_Read |  | 3x0038 | 1.00 | 0 | 25000 |  |  |  | Outdoor filter pressure [1/10 Pa]
| AHU controller | Summer Night Cooling | Standard | SN_SecondsOfActiveHeat |  | 3x0045 | 1.00 | 0 | 32000 |  |  |  | SummerNight Time with Heat Demand [sec]
| Heat Exchanger | Set point | Standard | HX_HT_PowerRegSet |  | 3x0046 | 1.00 | 0 | 10000 |  |  |  | Heat exchange controller heating power [1/100%]
| Heating Coil | Set point | Standard | HT_RH_PowerRegSet |  | 3x0047 | 1.00 | 0 | 10000 |  |  |  | Actual heating power [1/100%]
| Cooling Coil | Set point | Standard | CL_RC_PowerRegSet |  | 3x0048 | 1.00 | 0 | 10000 |  |  |  | Cooling controller power [1/100%]
| AHU controller | Set point | Standard | HX_CL_PowerRegSet |  | 3x0049 | 1.00 | 0 | 10000 |  |  |  | Cool exchange controller coolting power [1/100%]
| Fan, Supply | State of SA Fan | Standard | OL_SA_State |  | 3x0060 | 1.00 | 0 | 499 |  |  |  | Actual operating mode 000-099: Unit stopped 100-199: Unit in low speed mode 200-299: Unit in medium speed mode 300-399: Unit in high speed mode 400-499: Unit in spec. control mode
| Fan, Exhaust | State of EA Fan | Standard | OL_EA_State |  | 3x0061 | 1.00 | 0 | 499 |  |  |  | Actual operating mode 000-099: Unit stopped 100-199: Unit in low speed mode 200-299: Unit in medium speed mode 300-399: Unit in high speed mode 400-499: Unit in spec. control mode
| Rotary Heat Exchanger | Current value | Standard | DRHX_RpmOut |  | 3x0093 | 1.00 | 0 | 3000 |  |  |  | Rotary heat exchanger – speed output [1/10 rpm]
| Rotary Heat Exchanger | Current value | Standard | DRHX_Power_In |  | 3x0095 | 1.00 | 0 | 6000 |  |  |  | Rotary heat exchanger – output power [W] (only with OJ RHX2M)
| Rotary Heat Exchanger | Set point | Standard | DRHX_PercentSet |  | 3x0098 | 1.00 | 0 | 10000 |  |  |  | Rotary heat exchanger – percentage setpoint [1/100%] (only with OJ DRHX)
| AHU controller | Time | Standard | RTC_WeekDay |  | 3x0110 | 1.00 | 1 | 7 |  |  |  | Actual day of the week (1=Mon..7=Sun)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+0 |  | 3x0120 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack) AlrGrp AlrNo
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+1 |  | 3x0121 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+2 |  | 3x0122 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+3 |  | 3x0123 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+4 |  | 3x0124 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+5 |  | 3x0125 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+6 |  | 3x0126 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+7 |  | 3x0127 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+8 |  | 3x0128 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+9 |  | 3x0129 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+10 |  | 3x0130 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+11 |  | 3x0131 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+12 |  | 3x0132 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+13 |  | 3x0133 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+14 |  | 3x0134 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | Alarm | Standard | AL_Hist_GrpNum_AlrNum+15 |  | 3x0135 | 1.00 | 0 | 25100 |  |  |  | Stack for active alarms (0 indicates end of stack)
| AHU controller | SW version | Standard | SoftwareVersion |  | 3x0140 | 1.00 | 100 | 999 |  |  |  | Master software version [1/100]
| AHU controller | SW version | Standard | SoftwareBetaVersion |  | 3x0141 | 1.00 | 0 | 999 |  |  |  | Master software Betaversion [1/100]
| AHU controller | SW version | Standard | BootLoaderVersion |  | 3x0142 | 1.00 | 100 | 999 |  |  |  | Bootloader software version [1/100]
| Filter, Outdoor |  | Standard | FM_SF_OA_FM_Type_UserSet |  | 3x160 | 1.00 | 0 | 3 |  |  |  | 0-not filter, 1-Timer, 2-Static, 3-dynamic, 4-Switch
| Filter, Outdoor | Current value | Standard | FM_SF_OA_Status |  | 3x161 | 1.00 | 0 | 10000 |  |  |  | Outdoor filter monitor status [1/100%], ONLY IN DYNAMIC MODE FM_SF_OA_FM_Type_UserSet==3
| Filter, Outdoor | Current value | Standard | FM_SF_OA_Timer_Rest_h |  | 3x162 | 1.00 | 0 | 8800 |  |  |  | Hours until timer alarm from the outdoor filter, FM_SF_OA_FM_Type_UserSet==1
| Filter, Outdoor |  | Standard | FM_SF_OA_SwitchStatus |  | 3x163 | 1.00 | 0 | 1 |  |  |  | FM OA Filterswitch state, FM_SF_OA_FM_Type_UserSet==4
| Filter, Extract |  | Standard | FM_SF_EA_FM_Type_UserSet |  | 3x164 | 1.00 | 0 | 3 |  |  |  | 0-not filter, 1-Timer, 2-Static, 3-dynamic, 4-Switch
| Filter, Extract | Current value | Standard | FM_SF_EA_Status |  | 3x165 | 1.00 | 0 | 10000 |  |  |  | Outdoor filter monitor status [1/100%], ONLY IN DYNAMIC MODE FM_SF_EA_FM_Type_UserSet==3
| Filter, Extract | Current value | Standard | FM_SF_EA_Timer_Rest_h |  | 3x166 | 1.00 | 0 | 8800 |  |  |  | Hours until timer alarm from the outdoor filter, FM_SF_EA_FM_Type_UserSet==1
| Filter, Extract |  | Standard | FM_SF_EA_SwitchStatus |  | 3x167 | 1.00 | 0 | 1 |  |  |  | FM EA Filterswitch state, FM_SF_EA_FM_Type_UserSet==4
| Humidity, Extract | Current value | Standard | IOC_HUMI_EA_Read |  | 3x171 | 1.00 | 0 | 10000 |  |  |  | Actual % rel. Humidity Extract duct [1/100 %]
| 1. Info | 1. Info | 1. Info | 1. Info |  | Holding register (R/W) |  | 1. Info | 1. Info | 1. Info |  |  | 1. Info
| AHU controller | Set point | Standard | OL_ManualUserSet |  | 4x0001 | 1.00 | 0 | 5 |  |  |  | 0=Not active 1=Manual stop (1) 2=Manual low 3=Manual medium 4 =Manual high 5=extended Stop (2)
| AHU controller | Reg-Mode | Standard | AHU_SA_FanRegModeUserSet |  | 4x0002 | 1.00 | 0 | 7 |  |  |  | SA_FanRegMode 0 - Not mounted 1 - Flow 2 - Duct 3 - Demand (ppm) 4 - Fix Fan Speed 5 - Greenzone 6 - Slave 7 - Demand %rH
| AHU controller | Reg-Mode | Standard | AHU_EA_FanRegModeUserSet |  | 4x0003 | 1.00 | 0 | 7 |  |  |  | EA_FanRegMode 0 - Not mounted 1 - Flow 2 - Duct 3 - Demand (ppm) 4 - Fix Fan Speed 5 - Greenzone 6 - Slave 7 - Demand %rH
| AHU controller | Set point | Standard | PR_SA_LS_UserSet |  | 4x0004 | 1.00 | 200 | PR_SA_MED_UserSet |  |  |  | Setpoint for duct pressure, low supply [1/10Pa]
| AHU controller | Set point | Standard | PR_SA_MED_UserSet |  | 4x0005 | 1.00 | PR_SA_LS_UserSet | PR_SA_HS_UserSet |  |  |  | Setpoint supply air duct pressure medium speed [1/10Pa]
| AHU controller | Set point | Standard | PR_SA_HS_UserSet |  | 4x0006 | 1.00 | PR_SA_MED_UserSet | PR_SA_MS_UserSet |  |  |  | Setpoint for duct pressure, high supply [1/10Pa]
| AHU controller | Set point | Standard | PR_EA_LS_UserSet |  | 4x0010 | 1.00 | 200 | PR_EA_MED_UserSet |  |  |  | Setpoint for low duct pressure, extract [1/10Pa]
| AHU controller | Set point | Standard | PR_EA_MED_UserSet |  | 4x0011 | 1.00 | PR_EA_LS_UserSet | PR_EA_HS_UserSet |  |  |  | Setpoint exhaust air duct pressure medium speed [1/10Pa]
| AHU controller | Set point | Standard | PR_EA_HS_UserSet |  | 4x0012 | 1.00 | PR_EA_MED_UserSet | PR_EA_MS_UserSet |  |  |  | Setpoint for high duct pressure, extract [1/10Pa]
| AHU controller | Set point | Standard | AR_SA_LS_UserSet |  | 4x0015 | 1.00 | AHU_SA_MinFlow | AR_SA_MED_UserSet |  |  |  | Setpoint for supply flow, low speed [l/s]
| AHU controller | Set point | Standard | AR_SA_MED_UserSet |  | 4x0016 | 1.00 | AR_SA_LS_UserSet | AR_SA_HS_UserSet |  |  |  | Setpoint supply air flow - medium speed [l/s]
| AHU controller | Set point | Standard | AR_SA_HS_UserSet |  | 4x0017 | 1.00 | AR_SA_MED_UserSet | AR_SA_MS_UserSet |  |  |  | Setpoint for supply flow, high speed [l/s]
| AHU controller | Set point | Standard | AR_EA_LS_UserSet |  | 4x0019 | 1.00 | AHU_EA_MinFlow | AR_EA_MED_UserSet |  |  |  | Setpoint for extract flow, low speed [l/s]
| AHU controller | Set point | Standard | AR_EA_MED_UserSet |  | 4x0020 | 1.00 | AR_EA_LS_UserSet | AR_EA_HS_UserSet |  |  |  | Setpoint exhaust air flow - medium speed [l/s]
| AHU controller | Set point | Standard | AR_EA_HS_UserSet |  | 4x0021 | 1.00 | AR_EA_MED_UserSet | AR_EA_MS_UserSet |  |  |  | Setpoint for extract flow, high speed [l/s]
| AHU controller | Set point | Standard | FX_SA_LS_UserSet |  | 4x0023 | 1.00 | FX_SA_Min_Prc_UserSet | FX_SA_MED_UserSet |  |  |  | Supply Motor Lowspeed [1/100%], Fixed Fan Speed
| Fan, Supply | Set point | Standard | FX_SA_MED_UserSet |  | 4x0024 | 1.00 | FX_SA_LS_UserSet | FX_SA_HS_UserSet |  |  |  | Supply Motor Mediumspeed [1/100%], Fixed Fan Speed
| Fan, Supply | Set point | Standard | FX_SA_HS_UserSet |  | 4x0025 | 1.00 | FX_SA_MED_UserSet | FX_SA_Max_Prc_UserSet |  |  |  | Supply Motor Highspeed [1/100%], Fixed Fan Speed
| Fan, Exhaust | Set point | Standard | FX_EA_LS_UserSet |  | 4x0028 | 1.00 | FX_EA_Min_Prc_UserSet | FX_EA_MED_UserSet |  |  |  | Exhaust Motor Lowspeed [1/100%], Fixed Fan Speed
| Fan, Exhaust | Set point | Standard | FX_EA_MED_UserSet |  | 4x0029 | 1.00 | FX_EA_LS_UserSet | FX_EA_HS_UserSet |  |  |  | Exhaust Motor Mediumspeed [1/100%], Fixed Fan Speed
| Fan, Exhaust | Set point | Standard | FX_EA_HS_UserSet |  | 4x0030 | 1.00 | FX_EA_MED_UserSet | FX_EA_Max_Prc_UserSet |  |  |  | Exhaust Motor Highspeed [1/100%], Fixed Fan Speed
| AHU controller | Set point | Standard | SC_SlaveOffsetUserSet |  | 4x0033 | 1.00 | 500 | 2000 |  |  |  | Supply/extract motor offset, slave and CO2 control [1/100%]
| AHU controller | Set point | Standard | DC_LS_CO2_UserSet |  | 4x0036 | 1.00 | 0 | 2000 |  |  |  | CO2 control: setpoint for low period (low CO2 value) [ppm]
| AHU controller | Set point | Standard | DC_MED_CO2_UserSet |  | 4x0037 | 1.00 | 0 | 2000 |  |  |  | CO2 controller setpoint medium speed (med CO2 Val) [ppm]
| AHU controller | Set point | Standard | DC_HS_CO2_UserSet |  | 4x0038 | 1.00 | 0 | 2000 |  |  |  | CO2 control: setpoint for high period (high CO2 value) [ppm]
| AHU controller | Set point | Standard | VOC_LS_DemandUserSet |  | 4x0039 | 1.00 | 0 | 10000 |  |  |  | VOC control: setpoint for low period (low VOC value) [ppm]
| AHU controller | Set point | Standard | VOC_MED_DemandUserSet |  | 4x0040 | 1.00 | 0 | 10000 |  |  |  | VOC controller setpoint medium speed (med VOC Val) [ppm]
| AHU controller | Set point | Standard | VOC_HS_DemandUserSet |  | 4x0041 | 1.00 | 0 | 10000 |  |  |  | VOC control: setpoint for high period (high VOC value) [ppm]
| AHU controller | Set point | Standard | RH_LS_DemandUserSet |  | 4x0042 | 1.00 | 0 | 10000 |  |  |  | rH control: setpoint for low period (low CO2 value) [%rH]
| AHU controller | Set point | Standard | RH_MED_DemandUserSet |  | 4x0043 | 1.00 | 0 | 10000 |  |  |  | rH controller setpoint medium speed (med rH Val) [%rH]
| AHU controller | Set point | Standard | RH_HS_DemandUserSet |  | 4x0044 | 1.00 | 0 | 10000 |  |  |  | rH control: setpoint for high period (high rH value) [%rH]
| AHU controller | Set point | Standard | DC_SA_MinFlow_UserSet |  | 4x0045 | 1.00 | 100 | DC_SA_MaxFlow_UserSet |  |  |  | Demand Control SA Minflow in [1/l/s]
| AHU controller | Set point | Standard | DC_SA_MaxFlow_UserSet |  | 4x0046 | 1.00 | DC_SA_MinFlow_UserSet | 30000 |  |  |  | Demand Control SA Maxflow in [1/l/s]
| AHU controller | Set point | Standard | DC_EA_MinFlow_UserSet |  | 4x0047 | 1.00 | 100 | DC_EA_MaxFlow_UserSet |  |  |  | Demand Control EA Minflow in [1/l/s]
| AHU controller | Set point | Standard | DC_EA_MaxFlow_UserSet |  | 4x0048 | 1.00 | DC_EA_MinFlow_UserSet | 30000 |  |  |  | Demand Control EA Maxflow in [1/l/s]
| AHU controller | Set point | Standard | AHU_SA_GZM_Prc_Set |  | 4x0049 | 1.00 | 0 | 10000 |  |  |  | External signal GreenZone, supply [1/100%]
| AHU controller | Set point | Standard | AHU_EA_GZM_Prc_Set |  | 4x0050 | 1.00 | 0 | 10000 |  |  |  | External signal GreenZone, exhaust [1/100%]
| AHU controller | Set point | Standard | AR_SA_Reg_PB_UserSet |  | 4x0055 | 1.00 | 100 | 4000 |  |  |  | Flow-Regulator SA P-Band in [1/100%]
| AHU controller | Set point | Standard | AR_SA_Reg_It_UserSet |  | 4x0056 | 1.00 | 1 | 1800 |  |  |  | Flow SA I-Time in [1/1sec]
| AHU controller | Set point | Standard | AR_EA_Reg_PB_UserSet |  | 4x0057 | 1.00 | 100 | 4000 |  |  |  | Flow EA P-Band in [1/100%]
| AHU controller | Set point | Standard | AR_EA_Reg_It_UserSet |  | 4x0058 | 1.00 | 1 | 1800 |  |  |  | Flow EA I-Time in [1/1sec]
| AHU controller | Set point | Standard | PR_SA_Reg_PB_UserSet |  | 4x0059 | 1.00 | 100 | 4000 |  |  |  | Pressure SA P-Band in [1/100%]
| AHU controller | Set point | Standard | PR_SA_Reg_It_UserSet |  | 4x0060 | 1.00 | 1 | 1800 |  |  |  | Pressure SA I-Time in [1/1sec]
| AHU controller | Set point | Standard | PR_EA_Reg_PB_UserSet |  | 4x0061 | 1.00 | 100 | 4000 |  |  |  | Pressure EA P-Band in [1/100%]
| AHU controller | Set point | Standard | PR_EA_Reg_It_UserSet |  | 4x0062 | 1.00 | 1 | 1800 |  |  |  | Pressure EA I-Time in [1/1sec]
| AHU controller | Set point | Standard | DC_VOC_Reg_PB_UserSet |  | 4x0063 | 1.00 | 0 | 10000 |  |  |  | P-Band VOC [ppm]
| AHU controller | Set point | Standard | DC_CO2_Reg_PB_UserSet |  | 4x0064 | 1.00 | 0 | 10000 |  |  |  | P-Band CO2 [ppm]
| AHU controller | Set point | Standard | DC_Reg_It_UserSet |  | 4x0065 | 1.00 | 0 | 30000 |  |  |  | I-Time (VOC/CO2 [1/1sec]
| AHU controller | Summer Night Cooling | Standard | SN_AR_SA_Flow_UserSet |  | 4x0066 | 1.00 | AHU_SA_MinFlow | AR_SA_MS_UserSet |  |  |  | Setpoint supply air volume sommernight cooling
| AHU controller | Summer Night Cooling | Standard | SN_AR_EA_Flow_UserSet |  | 4x0067 | 1.00 | AHU_EA_MinFlow | AR_EA_MS_UserSet |  |  |  | Setpoint extract air volume sommernight cooling [m3/h]
| AHU controller | Summer Night Cooling | Standard | SN_PR_SA_Press_UserSet |  | 4x0068 | 1.00 | DUCT_PRESSURE_MIN | PR_SA_Max_Set |  |  |  | Setpoint supply air pressure sommernight cooling [Pa]
| AHU controller | Summer Night Cooling | Standard | SN_PR_EA_Press_UserSet |  | 4x0069 | 1.00 | DUCT_PRESSURE_MIN | PR_EA_Max_Set |  |  |  | Setpoint extract air pressure sommernight cooling [Pa]
| AHU controller | Summer Night Cooling | Standard | SN_FX_SA_Prc_UserSet |  | 4x0070 | 1.00 | FX_SA_Min_Prc_UserSet | FX_SA_Max_Prc_UserSet |  |  |  | Setpoint supply air constant speed sommernight cooling [1/100%]
| AHU controller | Summer Night Cooling | Standard | SN_FX_EA_Prc_UserSet |  | 4x0071 | 1.00 | FX_EA_Min_Prc_UserSet | FX_EA_Max_Prc_UserSet |  |  |  | Setpoint extract air constant speed sommernight cooling [1/100%]
| AHU controller | Fire | Standard | AH_Fire1_SA_PrcUserSet |  | 4x0080 | 1.00 | 0 | 10000 |  |  |  | Supply motor speed setpoint in case of fire alarm [1/100%]
| AHU controller | Fire | Standard | AH_Fire1_EA_PrcUserSet |  | 4x0081 | 1.00 | 0 | 10000 |  |  |  | Extract motor speed setpoint in case of fire alarm [1/100%]
| AHU controller | Fire | Standard | AH_FireInt_SA_TempSet |  | 4x0082 | 1.00 | 5000 | 12000 |  |  |  | Limit for SA Temperature internal Fire [1/100°C]
| AHU controller | Fire | Standard | AH_FireInt_EA_TempSet |  | 4x0083 | 1.00 | 3500 | 12000 |  |  |  | Limit for EA Temperature internal Fire [1/100°C]
| AHU controller | Control | Standard | TR_RegType_UserSet |  | 4x0090 | 1.00 | 0 | 3 |  |  |  | 0=not available,1-supply, 2-Extract, 3=Room
| AHU controller | Set point | Standard | TR_SA_Temp_UserSet |  | 4x0091 | 1.00 | 500 | 4000 |  |  |  | Temperature setpoint for Supply control type [1/100°C]
| AHU controller | Set point | Standard | TR_EA_Temp_UserSet |  | 4x0092 | 1.00 | 500 | 4000 |  |  |  | Temperature setpoint for Extract control type [1/100°C]
| AHU controller | Set point | Standard | TR_RM_Temp_UserSet |  | 4x0093 | 1.00 | 500 | 4000 |  |  |  | Temperature setpoint for Room control type [1/100°C]
| AHU controller | Set point | Standard | TR_EA_SA_MinTemp_UserSet |  | 4x0094 | 1.00 | 0 | 3000 |  |  |  | Min. limit supply temperature [1/100°C] Extract/Room
| AHU controller | Set point | Standard | TR_EA_SA_MaxTemp_UserSet |  | 4x0095 | 1.00 | 800 | 5000 |  |  |  | Max. limit supply temperature [1/100°C] Extract/Room
| AHU controller | Control | Standard | TR_EA_PB_UserSet |  | 4x0100 | 1.00 | 100 | 4000 |  |  |  | P-band for extract air temperature control [1/100°C]
| AHU controller | Control | Standard | TR_EA_It_UserSet |  | 4x0101 | 1.00 | 1 | 1800 |  |  |  | Heat / Cool I-Time for Extract-Regulator [1/sec]
| AHU controller | Control | Standard | TR_SA_CL_RC_PB_UserSet |  | 4x0102 | 1.00 | 100 | 4000 |  |  |  | P-Band for supply coolsource control [1/100°C]
| AHU controller | Control | Standard | TR_SA_CL_HX_PB_UserSet |  | 4x0103 | 1.00 | 100 | 4000 |  |  |  | P-Band for supply cool exchanger control [1/100°C]
| AHU controller | Control | Standard | TR_SA_HT_HX_PB_UserSet |  | 4x0104 | 1.00 | 100 | 4000 |  |  |  | P-Band for supply heat exchanger control [1/100°C]
| AHU controller | Control | Standard | TR_SA_HT_RH_PB_UserSet |  | 4x0105 | 1.00 | 100 | 4000 |  |  |  | P-Band for supply heatsource control [1/100°C]
| AHU controller | Control | Standard | TR_SA_HT_DNRG_PB_UserSet |  | 4x0106 | 1.00 | 100 | 4000 |  |  |  | P-Band for supply heat flowdown control [1/100°C]
| AHU controller | Control | Standard | TR_SA_CL_RC_It_UserSet |  | 4x0107 | 1.00 | 1 | 1800 |  |  |  | I-time for supply heat flowdown control [sec]
| AHU controller | Control | Standard | TR_SA_CL_HX_It_UserSet |  | 4x0108 | 1.00 | 1 | 1800 |  |  |  | I-time for supply cool exchanger control [sec]
| AHU controller | Control | Standard | TR_SA_HT_HX_It_UserSet |  | 4x0109 | 1.00 | 1 | 1800 |  |  |  | I-time for supply heat exchanger control [sec]
| AHU controller | Control | Standard | TR_SA_HT_RH_It_UserSet |  | 4x0110 | 1.00 | 1 | 1800 |  |  |  | I-time for supply heatsource control [sec]
| AHU controller | Control | Standard | TR_SA_HT_DNRG_It_UserSet |  | 4x0111 | 1.00 | 1 | 1800 |  |  |  | I-time for supply heat flowdown control [sec]
| AHU controller | Set point | Standard | CL_RC_MinOA_Tmp_UserSet |  | 4x0115 | 1.00 | -3000 | 3000 |  |  |  | Min. outdoor temperature for start of cooling
| AHU controller | Set point | Standard | OL_SU_HW_PowerUserSet |  | 4x0117 | 1.00 | 0 | 10000 |  |  |  | Heating coil: Startup power setpoint [1/100%]
| AHU controller | Set point | Standard | HT_RH_FP_AHU_StopUserSet |  | 4x0118 | 1.00 | 0 | 4000 |  |  |  | Setpoint for frost protection control when unit is in STOP mode [1/100°C]
| AHU controller | Set point | Standard | HT_RH_FP_AHU_RunUserSet |  | 4x0119 | 1.00 | 0 | 4000 |  |  |  | Setpoint for frost prot. control when unit is in OPERATING mode [1/100°C]
| AHU controller | Set point | Standard | HT_RH_FP_AlrLim_UserSet |  | 4x0120 | 1.00 | 0 | 4000 |  |  |  | Setpoint for frost protection temp. alarm [1/100°C]
| AHU controller | Time | Standard | RTC_YearUserSet |  | 4x0130 | 1.00 | 2000 | 2099 |  |  |  | Actual year
| AHU controller | Time | Standard | RTC_MonthUserSet |  | 4x0131 | 1.00 | 1 | 12 |  |  |  | Actual month
| AHU controller | Time | Standard | RTC_DateUserSet |  | 4x0132 | 1.00 | 1 | 31 |  |  |  | Actual date
| AHU controller | Time | Standard | RTC_HourUserSet |  | 4x0133 | 1.00 | 0 | 23 |  |  |  | Actual hour
| AHU controller | Time | Standard | RTC_MinuteUserSet |  | 4x0134 | 1.00 | 0 | 59 |  |  |  | Actual minutes
| AHU controller | Time | Standard | RTC_SecondUserSet |  | 4x0135 | 1.00 | 0 | 59 |  |  |  | Actual seconds
| AHU controller | Summer Night Cooling | Standard | SN_RM_StartTmpUserSet |  | 4x0140 | 1.00 | 0 | 4000 |  |  |  | Summer night extract/room temp. start [1/100°C]
| AHU controller | Summer Night Cooling | Standard | SN_RM_StopTmpUserSet |  | 4x0141 | 1.00 | 0 | 4000 |  |  |  | Summer night extract/room temp. stop [1/100°C]
| AHU controller | Summer Night Cooling | Standard | SN_OA_StopTmpUserSet |  | 4x0142 | 1.00 | 0 | 4000 |  |  |  | Summer night outdoor temp. start [1/100°C]
| AHU controller | Summer Night Cooling | Standard | SN_MinSA_TempUserSet |  | 4x0143 | 1.00 | 0 | 4000 |  |  |  | Summer night supply temp. control setpoint [1/100°C]
| AHU controller | Summer Night Cooling | Standard | SN_StartHourUserSet |  | 4x0144 | 1.00 | 0 | 23 |  |  |  | Summer night start [h]
| AHU controller | Summer Night Cooling | Standard | SN_StartMinuteUserSet |  | 4x0145 | 1.00 | 0 | 59 |  |  |  | Summer night start [min]
| AHU controller | Summer Night Cooling | Standard | SN_StopHourUserSet |  | 4x0146 | 1.00 | 0 | 23 |  |  |  | Summer night stop [h]
| AHU controller | Summer Night Cooling | Standard | SN_StopMinuteUserSet |  | 4x0147 | 1.00 | 0 | 59 |  |  |  | Summer night stop [min]
| AHU controller | Alarm | Standard | AH_SA_TempDiffAlrLimit |  | 4x0148 | 1.00 | 0 | 10000 |  |  |  | Alarm limit for temperature differential between supply setpoint and actual value [1/100°C]
Note on B1: Jens B. Antonsen: Modbus and BACnet parameters reflect current values on installed components in the actual AHU. The parameters are always present, but might not be active. Actual AHU components installed depends on the AHU manufacturer brand and model.
Note on D1: Jens B. Antonsen: Standard: Always included in OJ-Air2master. Special: Partly included in some private label variants. Check the AHU controller part. No. and the AHU manufactor documentation.
Note on G1: Jens B. Antonsen: Registers start at no. 1. Adresses start at no. 0. A typical mistake is R/W to a neighbour register.
Note on H1: Jens B. Antonsen: Number: Register is available in this software version and higher versions. x.xx: Register is available in this software and some lower versions.
Note on I1: Jens B. Antonsen: Minimum value. Lower values will be ignored.
Note on J1: Jens B. Antonsen: Maximum value. Higher values will be ignored.
Note on K1: Jens B. Antonsen: Default valule from OJ Electronics factory.